## Sheet1
DPIDE Parameters description
Device number | Data type | Function | Desrciption
PID_RUN | BOOL | Enabling the PID algorithm
SV | REAL | SV: Set Value | Target value / Setpoint
PV | REAL | PV: Provess value | Process value
PID_MODE | DWORD/ DINT | PID control mode | 0: Automatic control: When PID_MAN is turned from true to false, the output value (MV) then is involved in the automatic algorithm. 1: The parameters are tuned automatically for the temperature control. When the tuning of the parameters is complete, the device is automatically set to 0, and is filled in with the appropriate parameters Kc_Kp, Ti_Ki, Td_Kd, and Tf.
PID_MAN | BOOL | PID A/M mode | True: Manual: The MV is output according to the MOUT, but it is still in the range of the MV_MIN to the MV_MAX. When PID_MODE is set to 1, the setting is ineffective. False: Automatic: The MV is output according to the PID algorithm, and the output value is in the range of MV_MIN to MV_MAX.
MOUT_AUTO | BOOL | MOUT automatic change mode | True: Automatic: The MOUT varies with the MV. False: Normal: The MOUT deos not vary with the MV.
CYCLE | DWORD/ DINT | Sampling time (TS) Value range: 1~40,000 ms | When the instruction is scanned, the PID algorithm is implmented according to the sampling time, and the MV is refreshed. (The CPU module does not automatically judge time and execute the instruciton according to the sampling time). If CYCLE is less than 1, it will be count as 1. If CYCLE is greater than 40,000, it will be count as 40,000. When the instruction is used in the timed interrupt, the CPU module automatically implements the PID algorithm according to the interval between the tiimed interrupts, and the setting of CYCLE does not work.
Kc_Kp | REAL | Proportional gain (Kc or Kp) | It is the proportional gain. If the proportional gain is less than 0, Kc_Kp will be count as 0. If Kc_Kp is equal to 0 when the independent formula is used, the proportional control is not used.
Ti_Ki | REAL | Integral gain (Ti or Ki). Unit: Ti=Second; Ki=1/second | It is the integral gain. If the integral gain is less than 0, Ti_Ki will be count as 0. If Ti_Ki is equal to 0, the integral control is not used.
Td_Kd | REAL | Derivative gain (Td or Kd) Unit: Second | It is the derivative gain. If the derivative gain is less than 0, Td_Kd will be count as 0. If Td_Kd is equal to 0, the derivative control is not used.
Tf | REAL | Derivative action time constant (Tf) Unit: Second | It the derivative action time constant. If the derivative action time constant is less than 0, Tf will be count as 0. If Tf is equal to 0, the derivative action time control is not used. (Derivative smoothing)
PID_EQ | BOOL | Selection of a PID formula | True: Dependent formula ; False: Independent Formula
PID_DE | BOOL | Selection of the calculation of the PID derivative error | True: Using the variations in the PV to calculate the control value of the derivative (Derivative of the PV) False: Using the variations in the error value (E) to calculate the control value of the derivative (Derivative of the error value)
PID_DIR | BOOL | PID forward/reverse direction | True: Reverse action (E=SV-PV) ; False: Forward action (E=PV-SV)
ERR_DBW | REAL | Range within which the error value is count as 0 | The error value (E) is equal to SV−PV or PV-SV. If the setting value is 0, the function will not be enabled, otherwise the CPU module will check whether the present error value is less than the absolute value of ERR_DBW, and check whether the present error value meets the cross status condition. If the present error value is less than the absolute value of ERR_DBW, and meets the cross status condition, the present error value will be count as 0, and the PID algorithm will be implemented, otherwise the present error value will be brought into the PID algorithm according to the normal processing.
MV_MAX | REAL | Maximum output value | Suppose MV_MAX is set to 1,000. When the MV is greater than 1,000, 1,000 is output. The value in MV_MAX should be greater than that in MV_MIN. Otherwise, the maximum MV and the minimum MV will be reversed.
MV_MIN | REAL | Minimum output value | Suppose MV_MIN is set to -1,000. When the MV is less than -1,000, -1,000 is output. The value in MV_MIN should be less than that in MV_MAX. Otherwise, the maximum MV and the minimum MV will be reversed.
MOUT | REAL | Manual output value | MOUT and PID_MAN are used together. If PID_MAN is set to true, the MV will be output according to the MOUT, but it will be still in the range of the MV_MIN to the MV_MAX.
BIAS | REAL | Feedforward output value | It is used for the PID Feedforward.
I_MV (It occupies ten consecutive 32-bit devices.) | REAL | I_MV | The accumulated integral value is only for reference. It still can be cleared or modified according to users’ need. When the MV is greater than the MV_MAX, or when the MV is less than MV_MIN, the accumulated integral value in I_MV is unchanged.
|  | _MV+1 | The system records the previous error value.
|  | I_MV+2~ I_MV+5 | For system use only
|  | I_MV+6 | The system records the previous PV.
|  | I_MV+7~ I_MV+9 | For system use only
MV | REAL | Output value | The MV is within the range of MV_MIN and MV_MAX.